Request for Quotation (RFQ)

for

Supply, Installation, Testing and Commissioning of DG Set (250 KVA, 3 Phase) for COVID-19 Management

I. Summary of Deadlines

| Release of Request for Quotation | 12/10/2021 |
| --- | --- |
| Confirmation of interest due | 14/10/2021 |
| Request for clarifications received by | 15/10/2021 |
| Response to Request for clarifications | 16/10/2021 |
| Due date and time of bid submission | 19/10/2021 up to 24:00 Hrs. |
| Bid Evaluation completed | 21/10/2021 |
| Issue of Purchase Order (P.O.) to successful bidder | 22/10/2021 |

Note that CHRI reserves the right to modify this schedule as needed. All prospective bidders who have confirmed interest by the due date as above, will be notified of any changes simultaneously by email.

II. CHRI Statement of Business

Centre for Health Research and Innovation (CHRI) is a registered company (Not for profit) under section 8 of Companies Act 2013 with Ministry of Corporate Affairs. It is a PATH (An International nonprofit organization) affiliated organization.

CHRI is mainly focusing on system and service innovations. It focusses on saving lives and improving health, especially among women and children as India continues to have high maternal, newborn, child mortality, morbidity, and malnutrition. CHRI strategically mobilizes partners in India and take program interventions to scale focusing on verticals such as MNCHN, TB/HIV, Neglected Tropical Diseases and Malaria, and Vaccines.

CHRI follows a holistic and health-systems-oriented approach to strengthen the continuum of care across the public health space rather than restricting itself to a specific theme. It can involve advocacy for policies, technologies and resources that improve health services and delivery.

III. Purpose of RFQ

CHRI is implementing “COVID-19 Respiratory care coordination project” supported by NSE Foundation to improve access to oxygen and supply of other essential equipment in hospitals. NSE Foundation is a Section 8 company that undertakes the CSR activities of the National Stock Exchange of India Limited and its subsidiaries (NSE Group), with a broad vision to enhance the well-being of underprivileged and marginalized communities.

In order to implement the project, CHRI has planned to procure Equipment a per Schedule of Requirement below:

| Schedule No. | Brief Description of Equipment | Quantity (Nos.) | Location of Site/Facility |
| --- | --- | --- | --- |
| I | DG Set (250 KVA, 3 Phase) | 1 | New Sadar Hospital, Deoghar, Jharkhand |

The detailed Technical Specifications are mentioned in Annexure-A.

IV. Bidding Process

Bidders are advised to study the RFQ Documents carefully. Submission of the Bid shall be deemed to have been submitted after careful study and examination of all instructions, eligibility criteria, terms and conditions and required technical specifications included in the RFQ Documents with full understanding of its implications. Bids not complying with all the given clauses in this RFQ Documents or failure to furnish all information required by the RFQ Documents or submission of a bid not substantially responsive to the RFQ Documents in every respect will be at bidder’s risk and may result in the rejection of Bid.

V. Bid Submission

  - Bid must contain the complete address of firm, including contact number / email ID of the person who is authorized to submit the bid with his/her signatures.

  - Un-signed bids shall not be accepted.

  - All pages of the bid being submitted must be signed and sequentially numbered by the bidder irrespective of the nature of content of the documents.

  - Bids NOT submitted as per the specified format and nomenclature will be liable to be rejected.

  - Ambiguous bids will be out rightly rejected.

  - The interested bidders may submit their Bid to CHRI on or before the time mentioned in this RFQ Documents.

  - CHRI will not be responsible for any delay on the part of the Bidders in submission of the bids. Any bid received by CHRI after the prescribed deadline for submission of bids will be summarily rejected. No further correspondence in this regard will be entertained.

  - Financial bid should be prepared as per Annexure E given in the RFQ Documents.

  - Bidders shall indicate their rates in clear/visible figures as well as in words. In case of a mismatch, the rates written in words will prevail.

  - Bids complete in all respects and associated documents, must be submitted through email up to the due date and time as per Section XI. No physical document is to be submitted by the Bidders.

  - At any time prior to the last date for submission of bids, CHRI, may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, modify the RFQ Documents by an amendment.

  - Bids not quoted as per the format given by CHRI will be liable to be rejected.

  - Printed terms and conditions of the bidders will not be considered as forming part of their bid. In case terms and conditions as given in the RFQ Documents are not acceptable to any bidder, they should clearly specify the deviations in their bids.

VI. Financial Requirements

The Financial bids/quotation should contain schedule-wise unit price for supply of Equipment and related services (including inland freight, transit insurance and any other incidental cost for delivery of Equipment at site i.e. DDP-Unloaded at site) with related services, as per Technical Specifications (Annexure-A). The price should be quoted as per format given in Annexure-E.

VII. Delivery Schedule

The Equipment should be supplied and installed at designated Site/Facility within 45 days of issue of Purchase Order (P.O.)

Liquidated Damages (LD) for delay: In case handing over of plan is delayed beyond the delivery schedule as above, the LD @0.5% per day shall be levied, subject to standard force majeure conditions.

VIII. Payment Schedule

The payment shall be released within 30 days of submission of claim as per following schedule:

- 75% upon delivery of equipment at designated Site/Facility and submission of proof of delivery.

- 20% upon installation and user’s training and submission of Final Acceptance Certificate issued by the Hospital.

- 5% after 45 days of successful functioning of equipment and certificate to this effect issued by the Hospital.

IX. Bid Requirements – Technical

- Bidder’s eligibility requirements:

- Bidder should be a legal entity for doing business in India.

- Bidders should preferably be the manufacturer of quoted Equipment. In case bidder is not the manufacturer of the quoted Equipment, it should have authorization from manufacturer of Equipment or should be authorized distributor of original equipment manufacturer (OEM).

- Bidder should be in the business of supply and installation of DG Sets for last 3 (three) years as on the due date for submission of quotations and should have supplied and installed at least 3 Nos. DG Sets

- Technical Requirement:

The bidder should provide information on overall qualifications, including:

- Profile of organization covering relevant experience, number of years in business

- Past experience, clients handled and completed assignments.

- Services and support facilities available in major cities of India.

- Satisfactory performance certificates issued by Clients from at least 3 Clients

- The bidder should provide details for reference of at least three customers, to whom it would have supplied similar products during last three years as on the due date for submission of quotations.

Bid must be submitted in English language only and should contain:

- Letter of Bid with reference of all enclosures or attachments (as per Annexure B & C)

- Para-by-para compliance statement / no-deviation certificate against Technical Specifications given in Annexure-A

- Technical Particulars for 250 KVA Diesel Generator Set (as per Annexure-D)

- Financial Bid (as per Annexure-E)

- Mandatory enclosures as given below.

Mandatory enclosures:

Please submit the following as enclosures or attachment with the bid. If bidder do not submit these documents, their bid will not be considered for evaluation:

- Copy of registration documents/certificate as a legal entity in India.

- Copy of Work Order / Supply Order issued by Clients for supply of DG Sets during last 3 years as on the due date for submission of bids,

- Copy of manufacturer’s authorization issued by manufacturer of quoted equipment or authorized distributor certificate/letter issued by OEM, in case bidder is not the manufacturer.

- Complete technical offer including Make, Model and certifications in accordance with technical specifications.

- Quality Assurance Certificates as per Technical Specifications (Annexure-A)

- GST Registration copy

- Audited balance sheet and audit report for 3 financial years (2018-19, 2019-20 & 2020-21)

X. Bid Evaluation Criteria

- Bid evaluation process:

- Bids will be reviewed to determine completeness of bids (based on the RFQ Documents) and fulfillment to eligibility requirements of bidders. Bids that do not meet eligibility requirements will be eliminated following this review and not be considered further.

- All bids received by the stated closing date and time for bid submission will be evaluated and ranked, according to the conditions described in selection criteria below.

- The bids would be evaluated based on the prices quoted for total quantity of equipment under the Schedule. The final selection would be on the least cost selection basis subject to verification of documents and technical evaluation of the bids.

- Successful bidder will be notified in writing by email (or by telephone, in cases where the bidder is unable to be reached by email). Bidder must confirm acceptance in writing within the time specified in the email.

- Evaluation criteria:

- The bidders who substantially qualifies to the “Bid Requirements – Technical” (Section IX) shall be determined as technically qualified bidder.

- The bidder quoting lowest cost for a Schedule shall be considered for issue of P.O.

NOTE: CHRI reserves the right to reject bids that do not meet eligibility or bid submission requirements (as detailed above) without further notice to the bidders. Issuance of this RFQ does not constitute a commitment on the part of CHRI nor does it commit CHRI to pay for the costs incurred in submission of bid. Further, CHRI reserves the right to reject any or all bids received and to negotiate separately with a bidder, if such action is considered to be in the best interest of CHRI.

# XI. Instructions and Deadlines for Responding

A. CHRI contacts:

Any communication must be sent to: rfqngo.chri@gmail.com

B. Confirmation of interest:

Please send a statement acknowledging receipt of this solicitation and your intent to respond or not respond no later than due date given in Section-I. Send the confirmation to the contact listed above.

C. Request for clarifications:

Request for clarifications / questions on this solicitation will be accepted via email to the contact listed below through email by due date given in Section –I. Questions and answers will be provided to all prospective bidder who confirmed interest. Please note that responses will not be confidential except in cases where proprietary information is involved. Inquiries after this date cannot be entertained.

D.  Due date and time of Bid Submission :

Submit your completed bid by email to rfqngo.chri@gmail.com  latest by 21:00 Hrs. on 22nd October, 2021. The subject line of the email should read: Supply, Installation, Testing and Commissioning of DG Set (250 KVA, 3 Phase) for COVID-19 Management

We advise that bidders send files in commonly recognized Microsoft formats. We will not accept responsibility for resolving technical transmission problems with bids. A hard copy of the proposal should not be sent. Your bid should only include information specific to accomplishing the scope of work. Additional information submitted outside of the bid requirements will be reviewed at CHRI’s discretion only.

E. Selection of Bidder

CHRI reserves the right to select from among the bids received. CHRI has the option to interview and discuss specific details with those bidders who have submitted their bids.

F. Receipt, Evaluation and handling of bids

Once a bid is received before the due date and time, the CHRI will:

- log the receipt of the bids and record the business information

- review all bids and disqualify any non-responsive ones (that fail to meet the terms set out in RFQ Documents) and retain the business details on file with a note indicating disqualification.

- evaluate all bids objectively in line with the criteria specified in the RFQ Documents

- Inform bidders within timelines as per RFQ of the evaluation decision being made.

G. Conflict of Interest

  - Bidders must disclose in their bid, details of any circumstances, including personal, financial and business activities that will, or might, give rise to a conflict of interest. This disclosure must extend to all personnel proposed to undertake the work.

  - Where Bidders identify any potential conflicts, they must state how they intend to avoid any impact arising from such conflicts. CHRI reserves the right to reject any bid which, in the CHRI’s opinion, give rise, or could potentially give rise to, a conflict of interest.

  - With respect to this condition, please be advised that the organizations that may fall within the scope of this evaluation will include those below, with which any association must be disclosed:

H. General Disclosures

      - Bidders must disclose:

    - If they are or have been the subject of any proceedings or other arrangements relating to bankruptcy, insolvency or the financial standing of the bidders including but not limited to the appointment of any officer such as a receiver in relation to the Bidder personal or business matters or an arrangement with creditors or of any other similar proceedings.

    - If they have been convicted of, or are the subject of any proceedings, relating to:

      - Criminal offence or other offence, a serious offence involving the activities of a criminal organization or found by any regulator or professional body to have committed professional misconduct.

      - Corruption including the offer or receipt of any inducement of any kind in relation to obtaining any contract, with the CHRI, or any other contracting body or authority.

      - Failure to fulfil any obligations in any jurisdiction relating to the payment of taxes.

XII. Terms and Conditions

A. Notice of non-binding solicitation

CHRI reserves the right to reject any and all bids received in response to this solicitation, and is in no way bound to accept any bid.

B. Confidentiality

All information provided by CHRI as part of this solicitation must be treated as confidential. In the event that any information is inappropriately released, CHRI will seek appropriate remedies as allowed.

Bids, discussions, and all information received in response to this solicitation will be held as strictly confidential, except as otherwise noted.

C. Communication

All communications regarding this solicitation shall be directed to designated officials of CHRI. Bidders contacting third parties involved in the project, the review panel, or any other party may be considered a conflict of interest, and could result in disqualification of the bid.

D. Acceptance

Acceptance of a bid does not imply acceptance of its terms and conditions. CHRI reserves the option to negotiate on the final terms and conditions. We additionally reserve the right to negotiate the substance of the finalists’ bid, as well as the option of accepting partial components of a bid if appropriate.

E. Right to final negotiations

CHRI reserves the option to negotiate on the final costs and final scope of work, and also reserves the option to limit or include third parties at CHRI’s sole and full discretion in such negotiations.

F. Third-party limitations

CHRI does not represent, warrant, or act as an agent for any third party as a result of this solicitation. This solicitation does not authorize any third party to bind or commit CHRI in any way without our express written consent.

G. Bid Validity

Bid submitted under this request shall be valid for 1 month from the date the due date of bid submission. The bid validity period shall be stated in the bid submitted to CHRI.

XIII. Explanation to the Section I

| SL No. | Activity | Description |
| --- | --- | --- |
| 1 | Request for clarification | On or before the appointed date, all questions pertaining to the RFQ should be communicated to the CHRI through E mail. |
| 2 | Response on Request for clarification | On or before the appointed date, CHRI will address all queries to the applicants. |
| 3 | Applications due | This is the last date to receive application from the applicants. CHRI may not entertain any application post this date. |

Annexure A –Technical Specifications of Equipment

| Schedule No. I | DG Set (250 KVA, 3 Phase) |
| --- | --- |

| Sr. No. | Technical Specifications |
| --- | --- |
| 1. | Scope |
| 1.1 | The scope shall cover Supply, Installation & commissioning and training to consignee’s personnel. The offered equipment shall be of reputed make, type tested and shall be subjected to acceptance & routine tests in accordance with relevant standards, as applicable. |
| 1.2 | The equipment shall conform in all respect to the high standard of design and workmanship. The equipment shall be robust, rugged in design. In the event of offered equipment manufactured by different manufacturers, it will be responsibility of the bidder to fully coordinate the activities of each manufacturer in such a way that the complete offered equipment is manufactured, supplied & guaranteed for successful operation. |
| 1.3 | All the materials used for the manufacture of the equipment shall be of the best quality and the design and workmanship shall be of the highest order, to ensure satisfactory operation over its full life. The offered equipment shall be complete with all components & accessories necessary for their effective and trouble-free operation and for meeting technical requirements stipulated herein below. Such components & accessories shall be deemed to be within the scope of supply, irrespective of whether these are specifically brought out in this specification or not. |
| 1.4 | The 250 KVA “RTU” (Ready to use – Company/OEM assembled) Diesel Generating Set for 3 Phase, 4 Wire 415/230 V A.C., 50 C/S, 0.8 PF along with AMF Panel for automatic starting and running. The DG Set should be diesel driven and self-electric start. |
| 2 | Diesel Engine: |
| 2.1 | 250 KVA, Multi (6/12) cylinder, diesel engine should be generally in accordance with IS: 649/1514 or IS: 10002 (with latest amendments), conforming to ISO 3046/BS 5514 standards and shall be energy saving type star marked by BEE. |
| 2.2 | Capable of developing minimum 310 BHP at 1500 RPM rated for continuous duty with additional 10% overload capacity for one hour in any period of twelve hours of continuous operation at standard operating condition flexibly coupled to Alternator as per IS:13364 (with latest amendments). |
| 2.3 | It should be provided with water cooling system and electric self-starting arrangement with electronic governor. |
| 2.4 | Necessary standard accessories such as battery set 160 AH, 2x12 V with electric starting system, Fuel tank of suitable capacity (990 Ltr) for 12 hour running, coupling arrangement, cooling fan and radiator, mounting arrangement along with Anti-Vibration Mounting Pads should be provided. |
| 2.5 | Diesel Engine should be of reputed make like Greaves, Cummins, Catter Pillers, Ashok Leyland & Kirloskar or equivalent. |
| 2.6 | Engine Instrument Panel should have Start switch, Temperature gauge, Oil Pressure Gauge and other indication. DG set should have protection against under voltage, over voltage, under frequency, over frequency, low battery voltage, over current, earth fault, short circuit, phase sequence change etc. |
| 3 | Alternator |
| 3.1 | Alternator shall be self-excited and self-regulated, 250 kVA, 1500 RPM, 3 Phase 415 V, 50 C/S, 0.8 P.F conforming to IS: 13364 (with latest amendment thereof). |
| 3.2 | The alternator should be of reputed makes like NGEF, Kirloskar, Crompton, Stamford or equivalent with minimum insulation class-H, with digital automatic voltage regulator and IP 23 encloser. |
| 4 | Auto Mains failure (AMF) Panel |
| 4.1 | Control panel should be floor-mounting type, totally enclosed, dust and vermin proof, with degree of protection IP-53 as per IS/IEC: 60947(Part-1)2004, made-up of steel and comprising of Microprocessor based AMF relay, Timer, Contactor, Battery Charger complete with voltage regulator and KW/PF meter, Voltmeter and Ammeter for charging the battery from mains. This will be in addition to the battery charging alternator fitted on the engine. In addition to this, digital Frequency meter, Energy meter, Selector Switch, Phase Indicator, "Load on" and "Set Running" indicating lamps for each phase and suitable Protection arrangements, under voltage relay for mains, three attempt engine start/ engine cranking relay, on delay timer for load change over, on delay timer for engine shut off, Pilot lamps three nos., Instruments and control fuses 06 nos. power fuses of suitable rating, Audio visual alarm for low lubricating oil pressure, high water temperature, start failure and DG O/L, over current relay protection |
| 4.2 | “The AMF (Auto Mains Failure Panel) should be PLC (Programmable Logic Controller) based with capability of Engine Starts/Stop commands (both on auto and manual mode). There should be indicators/instruments showing Load on DG/Mains/Fault and Battery charger, Battery voltage, Fuel level indicator, Phase wise voltage with selector switches, Bus Voltage, frequency meter and all other standard accessories and by-pass changeover switch of suitable rating, complete in all respect suitable for 250KVA DG Set to ensure and its restoration respectively. The time for shutdown of DG Set after restoration of supply should be programmable based on the requirement of Consignee. All the accessories should be of reputed make”. |
| 4.3 | Along with the standard features of AMF Panel, the Auto- change over switch. All the arrangement along with changeover switch, cable, contractor, MCCB and all accessories shall be in the bidder’s scope. |
| 5 | Acoustic Canopy |
| 5.1 | Acoustic Canopy of reputed make should be provided for silent running. Container is fabricated out of CRCA sheet of 14 SWG. Sheet metal components are hot dip, 7-tanks pretreated and should be powder coated. |
| 5.2 | Acoustic Canopy should not have any protruding parts and specially designed to meet stringent MOEF/CPCB norms of 75 dBA @ 01 Mtr. at 75% load under free field conditions. |
| 5.3 | Sound proofing of enclosure is done with high quality rock wool / mineral wool conforming to IS: 8183 of 50 mm thickness and density at 96 kg / m3. The rock wool should be further covered with fiberglass cloth and perforated under coated sheet. |
| 5.4 | Attenuator should be provided to control sound at air entry to the container and exit from the container. Container should be pure polyester-based powder coated. Noise level should be as per standards laid down by MOEF/CPCB. Acoustic enclosure shall conform to pollution noise norms stipulated in notification GSR 371(E) Dt.17.05.2002, amended up to date |
| 6 | Accessories |
| 6.1 | Anti-Vibration mounting pads for Diesel Engine and Alternator. |
| 6.2 | 1 No. Fuel tank of suitable capacity for 12 Hrs. of continuous running provided with drain valve, air vent, inlet and outlet connections. |
| 6.3 | Batteries 160 AH 2x12 V, 25 plates of reputed make like Exide, Tata Green, Cummins or SF with battery connecting leads and terminals |
| 6.4 | Engine- Alternator Coupling guard |
| 6.5 | Necessary cables (30 Meters) for interconnections and installation |
| 6.6 | Change over switch. |
| 6.7 | Tool Kit |
| 7 | Installation and Commissioning: |
| 7.1 | Bidder will have to install and commission DG Sets along with all its accessories including foundation (platform), earthing, installation of fuel tank, battery charging and battery connection, fitting of exhaust pipe on the site / sites. Also, bidder will have to supply all accessories such as cables required for installation such as T-joint, pipes etc. |
| 8 | Warranty / Maintenance Services |
| 8.1 | The bidder shall provide warranty / comprehensive maintenance services for the duration of 3 (three) years form the date of successful installation and commissioning of the equipment. |
| 8.2 | During warranty / comprehensive maintenance services the bidder shall make quarterly visit the site for preventive maintenance of the equipment |
| 8.3 | The scope of warranty / comprehensive maintenance services shall cover batteries, filters and all accessories, parts required for smooth functioning of the equipment. |

Annexure B – Letter of Bid

To,

Centre for Health Research and innovation (CHRI)

Apeejay Business Centre, Arunachal Building, 6th floor,

Barakhamba Road,

New Delhi - 110001

Sub: Bid for Supply, Installation, Testing and Commissioning of DG Set (250 KVA, 3 Phase) for COVID-19 Management

Dear Sir,

- Having examined the RFQ Documents and appendix thereto, we, the undersigned, in conformity with the said document, offer to provide the said goods and associated services as given in the RFQ Documents and the terms of reference to be signed upon the award of contract as per the table below;

| Schedule No. | Brief Description of Equipment | Make & Model |
| --- | --- | --- |

- We undertake, if our bid is accepted for Supply, Installation, Testing and Commissioning of DG Set (250 KVA, 3 Phase) within time frame specified, starting from the date of receipt of issue of Purchase Order (P.O.) from CHRI.

- We agree to execute a P.O. in the form to be communicated by CHRI, incorporating all agreements with such alterations or additions thereto as may be necessary to adapt such agreement to the circumstances of the standard and notice of the award within time prescribed after notification of your intention to accept this bid.

- We would like to clearly state that we qualify for this work as we meet all the eligibility requirements indicated by you in the RFQ Documents.

- We certify that all the information mentioned in Annexure A of this covering letter is true and correct.

- We understand that if the details given in support of claims made above are found to be untenable or unverifiable or both our bid may be rejected without any reference to us. We further clearly understand that CHRI is not obliged to inform us of the reasons of rejection of our bid.

- It is certified that the information furnished herein and as per the document submitted is true and correct and nothing has been concealed or tampered with. We have gone through all the conditions of bid and are liable to any punitive action for furnishing false information/documents.

Dated this _____ day of 2021

Signature

(Bidder’s Seal)

__________________

In the capacity of

Duly authorized to sign bid  for and on behalf of:

Annexure C - Particulars of Bidder

- Name of the Supplier: _________________________________________________

- Address of the Supplier: _________________________________________________ _______________________________________District ______________ PIN _____________

- Email Address: ________________________________________________

- Phone: _________________________________________________

- Incorporated as: _______________ in year ___________ at ______________ (Company, State Registered Firm, Co-operative Society or Partnership Firm)

- Whether any Legal Arbitration/proceeding is instituted against the bidder or the bidder  has lodged any claim in connection with works carried out by them (Yes/No): ___________

- If yes, please give details. __________________________________________________

- Whether the bidder complies with the requirement of Registration under the Contract Labour (Regulation and Abolition) Act (Yes/No): __________________

- Bidder’s profile (*)

  - Name of the top executive: ___________________________________________

  - Designation: __________________________________________

  - Email Address: ___________________________________________

  - Mobile Number: ___________________________________________

  - Office Strength Technical: __________ Nos.

  - Administrative: __________ Nos.

- Bidder’s Turnover (In Rs.)

| 2018-19 |  |
| --- | --- |
| 2019-20 |  |
| 2020-21 |  |

Documents in support of the above may be furnished with page numbers indicated in the index. Please use separate sheets wherever necessary.

Date

Place

Bidder’s Seal

Annexure-D: Technical Particulars for 250 KVA Diesel Generator Set

| ENGINE |
| --- |
| 1 | Make |  |
| 2 | Model |  |
| 3 | BHP at Rated RPM |  |
| 4 | Rated RPM |  |
| 5 | No. of Cylinders |  |
| 6 | Bore/Stroke |  |
| 7 | Maximum Torque |  |
| 8 | Maximum BHP |  |
| 9 | Cooling/ Coolant Capacity (Engine + Radiator) |  |
| 10 | Pressure Ratio |  |
| 11 | Aspiration |  |
| 12 | Starting System |  |
| 13 | Lubricating Oil Capacity |  |
| 14 | Lubricating oil Consumption in Ltr. per hour for full load operation considering oil gravity 0.89 |  |
| 15 | Fuel tank capacity |  |
| 16 | Whether provided with drain valve, air vent, inlet and outlet connections in fuel tank. |  |
| 17 | Fuel Consumption in Ltr. per hour for 75% full load operation. |  |
| 18 | Battery rating (Voltage & Ah) |  |
| 19 | Over loading |  |
| 20 | Air Cleaner |  |
| 21 | Displacement |  |
| 22 | Output prime |  |
| ALTERNATOR: |
| 1 | Make |  |
| 2 | Model |  |
| 3 | No. of Phases |  |
| 4 | Frequency |  |
| 5 | Electrical Output in kVA for continuous operation at rated RPM 415 Volt 0.8 power factor (lagging) suitable for 50 Hz 3 phase 4 wire system). |  |
| 6 | Voltage corresponding to rated output |  |
| 7 | Percentage Voltage Regulation in static conditions. |  |
| 8 | Static excitation system |  |
| 9 | Insulation |  |
| 10 | Standard enclosure |  |
| 11 | Winding pitch |  |
| 12 | State & winding |  |
| 13 | Rotator |  |
| 14 | Telephone Interference factor |  |
| 15 | Total Harmonic factor |  |
| AMF CONTROL PANEL |
| 1 | Gauge of CRC Sheet used in panel |  |
| 2 | Whether painted with powder coated paint. |  |
| 3 | Whether provided with Automatic change over switch. |  |
| 4 | Whether provided with Ammeter |  |
| 5 | Whether provided with "Load on" and "Set Running" indicating lamps for each phase. |  |
| 6 | Details of protection provided. |  |
|  | a) For Genset‟s supply |  |
|  | b) For Mains‟ Supply |  |
|  | c) For prevention of Mixing of Generator and Mains‟ Supplies |  |
| 7 | Whether provided with Voltmeter |  |
| 8 | Whether provided with Battery Charger |  |
| 9 | Whether provided with Energy Meter |  |
| 10 | Whether provided with digital Frequency Meter |  |
| 11 | Whether provided with Phase Indicators |  |
| 12 | Whether provided with PLC (Programmable Logic Controller) based with capability of Engine Start/ Stop commands (both on auto and manual mode) |  |
| 13 | Whether provided with Indicators/ Instruments showing Load on DG / Mains/ Fault and Battery Charger/ Battery Voltage /Fuel Label Indicator, Phase wise voltage with selector switches, Bus Voltage, Mains Voltage, Frequency Meter and all other standard accessories. |  |
| 14 | Whether provided with by Pass Change over switch of suitable rating complete in all respect for 250 KVA DG Set to ensure automatic Start/Stop of the GENSET in the case of AC Mains Failure and its restoration respectively. |  |
| 15 | Whether provided with the time for shut down of DG Set after restoration of supply, programmable based on the requirement of CSPDCL. |  |
| 16 | Whether provided with all the accessories of reputed make. |  |
| ACOUSTIC CANOPY |
| 1 | Name of Manufacturer |  |
| 2 | Thickness of CRCA sheet used |  |
| 3 | Whether sheet metal components are hot dip, 7-tanks pretreated. |  |
| 4 | Thickness and density of rock wool / mineral wool. |  |
| 5 | Whether Sound proofing of enclosure is done with high quality rock wool / mineral wool conforming to IS:8183 |  |
| 6 | Whether rock wool covered with fiberglass cloth and perforated under coated sheet |  |
| 7 | Whether Attenuator are provided. |  |
| 8 | Whether polyester based powder coating is used. |  |
| 9 | Noise level at 3 mts. distance |  |
| OTHERS |
| 1 | How many Anti Vibration Pads will be provided? |  |
| 2 | Battery make, voltage, no. of plates, AH |  |
| 3 | Weight of assembled alternator and engine. |  |
| 4 | Dimensions |  |

Annexure E – Financial Bid

| Schedule No. | Brief Description of Equipment | Make & Model | Unit Rate (exclusive of GST) (INR) | GST Rate | GST Amount | Total Unit Price (inclusive of GST) (in figures) | Total Unit Price (in words) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | B | C | D | E | F | G (D+F) | H |
| I | Supply, Installation, Testing and Commissioning of DG Set (250 KVA, 3 Phase) and related services (as per Technical Specifications given in Annexure-A) |  |  |  |  |  |  |

- The rates quoted should be as per industry standards. Bids quoting zero or abnormally low rates compared to the industry prevalent rates will be rejected

- The rates finalized will not be changed throughout the period of bid validity.

Name of Supplier:

Authorized Signatory:

Name

Date

Place

Bidder’s Seal